Model Formulation for the Liquid-Cooled Chip Loop, Pump, and Compute Heat Exchanger

The chip loop, pump, and compute-side plate heat exchanger (HXer) are implemented in CHIPCOOLING.py with modular @dataclass components and a driver function compute_selected_with_branches_and_hx that calls each compute() in sequence and passes heat load, mass flow, temperatures, and pressure drops.

Liquid-Cooled Chip Surfaces

Inputs: GPUs N, thermal power per GPU​ PGPU [W], coolant inlet and outlet temperatures T1 and T2 [°C], density ρ [kg/m3]. The total chip heat load is:

Qchip=NPGPU

Water heat capacity at Tmean=(T1+T2)/2 is from a Shomate polynomial (molar) converted to mass basis to give Cp,chip, and for prescribed rise ∆Tc=T2-T1,

mc=QchipCp,chip∆Tc

Output: Qchip, Qp,chip, mc, ∆Tc

Hydraulic Network and Pump

GpuBranches input: mc, ρ, pipe data (Di, Li, fi) for rack, branch, header, and layout controls. The code assigns GPUs to racks, determine branches, splits mc, then for segment i:

Ai=πDi24,       vi=miρAi,  ∆pi=fiLiDiρvi22

The total pressure rise is ∆ppath=i∆pi.

Pump inputs: mc, , ρ, ∆ppath, ηp
Wpump=mcρ∆ppath​ηp

Compute Heat Exchanger (Compute HXer)

Counterflow plate HX coupling the chip loop to building water.

Notional building outlet (full chip load):

Tbout,full=Tbin+QchipmbCp,bldg

Design limit – UA-LMTD:
QUA=FcorrUA∆Tlm,  ∆Tlm=∆T1full-∆T2ln∆T1full∆T2

∆T1full=T2-Tbout,full,  ∆T2=T1-Tbin

Effectiveness (flow configuration/geometry) limit – ϵ-NTU:

Qϵ=ϵCminT2-Tbin,  Cmin=min(mcCp,chip, mbCp,bldg)

Implemented duty and tower inlet:

QHX=minQchip, QUA, Qϵ,  Ttower=Tbin+QHXmbCp,bldg

Simulation inputs:

| Number of GPUs (Meta) | 350,000 (Lee, Gangidi, & Oldham, 2024) |
| --- | --- |
| Thermal Power per GPU (H100 SXM) | 700 W (NVIDIA, 2024) |
| Mass Rate from Building/HX | 47778 kg/s |
| Temperature form Building to HX | 10 °C |
| Temperature for Chip Loop Inlet to Chip | 15 °C |
| Temperature for Chip Loop Outlet from Chips | 40 °C |
| GPUs per Rack/Branch | 8/32 |

Simulation outputs:

| Heat at Chips | 2.45E5 kW |
| --- | --- |
| mc | 2343.266 kg/s |
| Pump Power | 26.232 kW |
| Temperature from HX to Cooling Tower | 11.22 °C |
| Flow Rate from HX to Cooling Tower | 47778 kg/s |

References:
Lee, K., Gangidi, A., & Oldham, M. (2024, March 12). Building Meta’s GenAI infrastructure. Engineering at Meta. https://engineering.fb.com/2024/03/12/data-center-engineering/building-metas-genai-infrastructure/

NVIDIA. NVIDIA H100 GPU. Retrieved November 24, 2025, from https://www.nvidia.com/en-us/data-center/h100/