# HVAC Code Architecture Reference

Mapping Equations to Implementation

# 1. File Structure Overview

The HVAC system is implemented across the following files:

| File | Purpose |
| --- | --- |
| cooling_system.py | Main HVAC module: Chiller, Cooling Tower, Pumps, Integration |
| psychrometrics.py | Moist air property calculations (humidity, enthalpy, etc.) |
| main.py | System integration with Building HX and Chip Cooling |

# 2. Class Hierarchy in cooling_system.py

| Class | Responsibility |
| --- | --- |
| RefrigerantState | Calculates state properties (P, T, h, s, ρ, Q) using CoolProp |
| VaporCompressionCycle | Solves 4-state refrigeration cycle (States 1→2→3→4→1) |
| HeatExchanger | Effectiveness-NTU method for evaporator/condenser |
| Chiller | Couples refrigerant cycle with water loops, iterative solver |
| CoolingTower | Psychrometric analysis, evaporative heat rejection |
| Pump | Calculates pump power from fluid dynamics |
| CoolingSystem | Integrates all components, main solver interface |

# 3. Refrigerant Cycle: Equation to Code Mapping

## 3.1 RefrigerantState Class

Uses CoolProp's PropsSI function to calculate all thermodynamic properties:

self.P = PropsSI('P', input1, val1, input2, val2, refrigerant)

self.h = PropsSI('H', input1, val1, input2, val2, refrigerant)

self.s = PropsSI('S', input1, val1, input2, val2, refrigerant)

## 3.2 VaporCompressionCycle.solve() Method

State 1 - Evaporator Outlet (Superheated Vapor):

P_evap = PropsSI('P', 'T', T_evap_C + 273.15, 'Q', 1.0, refrigerant)

T1_C = T_evap_C + self.superheat_evap  # Add 5°C superheat

self.state1 = RefrigerantState(refrigerant, P=P_evap, T=T1_C)

State 2s - Isentropic Compression:

P_cond = PropsSI('P', 'T', T_cond_C + 273.15, 'Q', 0.0, refrigerant)

self.state2s = RefrigerantState(refrigerant, P=P_cond, s=self.state1.s)

State 2 - Actual Compression (Eq. 6):

h2_actual = self.state1.h + (self.state2s.h - self.state1.h) / self.eta_is_comp

self.state2 = RefrigerantState(refrigerant, P=P_cond, h=h2_actual)

State 3 - Condenser Outlet (Subcooled):

T3_C = T_cond_C - self.subcool_cond  # Subtract 3°C subcooling

self.state3 = RefrigerantState(refrigerant, P=P_cond, T=T3_C)

State 4 - Expansion (Isenthalpic):

self.state4 = RefrigerantState(refrigerant, P=P_evap, h=self.state3.h)

## 3.3 Energy Calculations

Mass flow rate (Eq. 17):

q_evap_per_kg = self.state1.h - self.state4.h

m_dot_ref = Q_evap_required / q_evap_per_kg

Evaporator heat (Eq. 11):

Q_evap = Q_evap_required  # Given input

Compressor work (Eq. 12):

W_comp = m_dot_ref * (self.state2.h - self.state1.h)

Condenser heat (Eq. 13):

Q_cond = m_dot_ref * (self.state2.h - self.state3.h)

COP (Eq. 16):

COP = Q_evap / W_comp

Energy balance verification (Eq. 15):

energy_balance_error = abs(Q_cond - (Q_evap + W_comp)) / Q_cond

# 4. Cooling Tower: Equation to Code Mapping

## 4.1 psychrometrics.py - MoistAir Class

Saturation pressure (Eq. 23 - Antoine equation):

ln_Pws = C1/T_K + C2 + C3*T_K + C4*T_K**2 + C5*T_K**3 + C6*math.log(T_K)

P_sat = math.exp(ln_Pws)

Humidity ratio (Eq. 24):

w = 0.622 * P_v / (P - P_v)

Specific enthalpy (Eq. 25):

h = CP_DA * T_C + w * (H_FG_0 + CP_WV * T_C)

# Where CP_DA = 1006, H_FG_0 = 2501000, CP_WV = 1860

## 4.2 CoolingTower.solve() Method

Water outlet temperature (Eq. 28):

t_out = self.calculate_outlet_temp(t_wb)  # = t_wb + approach

Air inlet/outlet states:

air_in = PsychrometricState(T_db_C=t_db, T_wb_C=t_wb)

air_out = PsychrometricState(T_db_C=t_out, RH=0.95)  # Near saturation

Water-side heat (Eq. 29):

q_water = m_dot_cw * self.cp_water * delta_t

Air mass flow from energy balance (Eq. 31):

delta_h_air = air_out.h - air_in.h

m_dot_da = q_water / delta_h_air  # Ensures Q_water = Q_air

Evaporation rate (Eq. 33):

m_evap = m_dot_da * (air_out.w - air_in.w)

Blowdown (Eq. 35):

m_blowdown = m_evap / (self.coc - 1)

Makeup water (Eq. 36):

m_makeup = m_evap + m_drift + m_blowdown

Fan power (Eq. 37):

w_fan = q_cond * 0.007  # 0.7% of heat rejected

# 5. System Integration: CoolingSystem.solve()

The iterative solution in CoolingSystem.solve() couples chiller and tower:

# Initial estimate

t_cw_in = t_wb_ambient_C + self.cooling_tower.approach + 0.5

for iteration in range(self.max_iter):

# Step 1: Solve chiller

chiller_result = self.chiller.solve_energy_balance(

q_evap=q_cooling_load_W, m_dot_chw=m_dot_chw_kg_s,

m_dot_cw=m_dot_cw, t_cw_in=t_cw_in, ...)

# Step 2: Solve cooling tower

tower_result = self.cooling_tower.solve(

q_cond=chiller_result['Q_cond_MW'] * 1e6,

m_dot_cw=m_dot_cw, t_in=chiller_result['T_cw_out_C'],

t_wb=t_wb_ambient_C, ...)

# Step 3: Check convergence

t_cw_in_new = tower_result['T_water_out_C']

if abs(t_cw_in_new - t_cw_in) < self.tol_C:

converged = True

break

t_cw_in = t_cw_in_new  # Update for next iteration

# 6. Input/Output Interface

## 6.1 CoolingSystem.solve() Inputs

| Parameter | Type/Unit | Description |
| --- | --- | --- |
| q_cooling_load_W | float [W] | Required cooling capacity |
| m_dot_chw_kg_s | float [kg/s] | Chilled water mass flow rate |
| t_chw_return_C | float [°C] | Return water temp from downstream HXs |
| t_wb_ambient_C | float [°C] | Ambient wet bulb temperature |
| t_db_ambient_C | float [°C] | Ambient dry bulb temperature (optional) |

## 6.2 CoolingSystem.solve() Output Structure

The output is a nested dictionary with two main sections:

result['downstream_interface']  # For Building HX / Chip HX

- T_chw_supply_C: 7.0

- T_chw_return_C: input value

- m_dot_chw_kg_s: input value

- Q_cooling_MW: cooling capacity

- system_COP: calculated

- total_power_MW: sum of all power consumers

result['internal_states']  # Detailed component results

- convergence: {converged, iterations}

- chiller: {Q_evap_MW, W_comp_MW, Q_cond_MW, COP, ...}

- condenser_water_loop: {m_dot_cw, T_cw_from_tower, ...}

- cooling_tower: {W_fan_MW, m_makeup_kg_s, ...}

- pump: {P_pump_W, ...}

- energy_balance: {error_pct}

# 7. Integration in main.py

The main.py file demonstrates how HVAC connects to other systems:

# Step 1: Initialize cooling system

cooling_system = CoolingSystem(

chiller_capacity_MW=1000.0,

chiller_cop=6.0,

t_chw_supply_C=7.0,

tower_approach_C=4.0,

tower_coc=4.0,

)

# Step 2: Calculate total cooling load

Q_total = Q_chip + Q_building  # 900 MW + 100 MW

# Step 3: Calculate CHW flow rate

m_dot_chw = Q_total / (Cp_water * deltaT_design)

# Step 4: Water flows through Building HX first

T_after_building = 7.0 + Q_building / (m_dot_chw * Cp_water)

# Step 5: Then through Compute HX

chip_result = compute_with_branches_and_hx(

T_bin=T_after_building, ...)  # Water enters Compute HX

T_after_compute = chip_result['T_to_tower_C']

# Step 6: Return water to chiller

cooling_result = cooling_system.solve(

q_cooling_load_W=Q_total,

m_dot_chw_kg_s=m_dot_chw,

t_chw_return_C=T_after_compute,  # ~12°C

t_wb_ambient_C=24.0,

)

# 8. Key Physical Constants Used

| Constant | Value | Description |
| --- | --- | --- |
| cp_water | 4186 J/(kg·K) | Water specific heat |
| h_fg | 2.26×10⁶ J/kg | Latent heat of vaporization |
| CP_DA | 1006 J/(kg·K) | Dry air specific heat |
| CP_WV | 1860 J/(kg·K) | Water vapor specific heat |
| H_FG_0 | 2.501×10⁶ J/kg | Latent heat at 0°C reference |
| P_ATM | 101325 Pa | Standard atmospheric pressure |
| rho_water | 998 kg/m³ | Water density |
| eta_is_comp | 0.80 | Compressor isentropic efficiency |
| eta_pump | 0.85 | Pump efficiency |