HVAC Cooling System for 1 GW AI Data Center

Abstract

This report presents the detailed thermodynamic modeling of the HVAC cooling system designed for a 1 GW AI data center. The system consists of a vapor compression chiller utilizing R134a refrigerant, an induced-draft cooling tower based on psychrometric analysis, and associated pump systems. The chiller provides 1000 MW of cooling capacity with a coefficient of performance (COP) of approximately 5.4, while the cooling tower rejects the condenser heat to the ambient environment through evaporative cooling. This document describes the governing equations, state point calculations, energy and mass balance considerations, key assumptions, and the interface with downstream building and chip heat exchangers.

Nomenclature

| Symbol | Description |
| --- | --- |
| Q̇ | Heat transfer rate [W] |
| Ẇ | Power [W] |
| ṁ | Mass flow rate [kg/s] |
| h | Specific enthalpy [J/kg] |
| s | Specific entropy [J/(kg·K)] |
| T | Temperature [°C or K] |
| P | Pressure [Pa] |
| w | Humidity ratio [kg water/kg dry air] |
| η | Efficiency [-] |
| COP | Coefficient of Performance [-] |
| c_p | Specific heat at constant pressure [J/(kg·K)] |
| h_fg | Latent heat of vaporization [J/kg] |

Subscripts

| evap | Evaporator |
| --- | --- |
| cond | Condenser |
| comp | Compressor |
| ref | Refrigerant |
| CHW | Chilled Water |
| CW | Condenser Water |
| da | Dry Air |
| wb | Wet Bulb |
| sat | Saturation |
| is | Isentropic |

1. Introduction

1.1 System Overview

Figure 1 System Diagram

The HVAC system serves as the primary cooling infrastructure for a modern AI data center with a total cooling load of 1 GW. The cooling architecture employs two independent water circulation loops shown in Figure 1:

Chilled Water (CHW) Loop: This closed-loop system circulates chilled water from the chiller evaporator through downstream heat exchangers (Building HX and Chip HX) and returns to the chiller. The supply temperature is maintained at 7°C with a design return temperature of 12°C.

Condenser Water (CW) Loop: This loop connects the chiller condenser to the cooling tower, rejecting the combined evaporator heat load and compressor work to the atmosphere through evaporative cooling.

1.2 Design Requirements

The HVAC system must satisfy the following design criteria:

- Total cooling capacity: 1000 MW (1 GW)

- Chilled water supply temperature: 7°C

- Design wet bulb temperature: 24°C

- Cooling tower approach temperature: 4°C

- Target PUE: < 1.3

2. Chiller System Modeling

The chiller system is modeled using a rigorous thermodynamic approach based on the vapor compression refrigeration cycle. The model employs CoolProp, an open-source thermodynamic property library, to calculate accurate refrigerant state properties throughout the cycle.

2.1 Vapor Compression Cycle Theory

The vapor compression refrigeration cycle consists of four main processes operating between the evaporator and condenser:

Process 1→2 (Compression): Low-pressure superheated vapor from the evaporator is compressed to high-pressure superheated vapor. The actual compression process accounts for irreversibility through the isentropic efficiency.

Process 2→3 (Condensation): High-pressure vapor is cooled and condensed in the condenser, rejecting heat to the condenser water. The refrigerant exits as subcooled liquid.

Process 3→4 (Expansion): High-pressure liquid is throttled through an expansion valve to low pressure. This isenthalpic process produces a two-phase mixture.

Process 4→1 (Evaporation): The two-phase refrigerant absorbs heat from the chilled water, evaporating completely and achieving slight superheat before entering the compressor.

2.2 State Point Calculations

Each state point in the cycle is uniquely defined by two independent thermodynamic properties. The RefrigerantState class implements these calculations using CoolProp:

2.2.1 State 1 - Evaporator Outlet (Superheated Vapor)

State 1 represents superheated vapor exciting the evaporator. The saturation pressure is determined from the evaporation temperature, and superheat is added to ensure complete vaporization:

P₁ = Psat(Tevap)     (1)

T₁ = Tevap + ΔTsuperheat     (2)

where ΔTsuperheat = 5°C is the design superheat. The remaining properties (h₁, s₁, ρ₁) are calculated from P₁ and T₁ using CoolProp.

2.2.2 State 2s - Isentropic Compression Outlet

State 2s represents the theoretical outlet condition for isentropic compression:

P₂ = Psat(Tcond)     (3)

s₂s = s₁     (4)

The isentropic outlet enthalpy h2 s is determined from P₂ and s₂s.

2.2.3 State 2 - Actual Compression Outlet

The actual compressor outlet accounts for irreversibility through the isentropic efficiency:

ηis = (h₂s - h₁) / (h₂ - h₁)     (5)

Rearranging to solve for actual outlet enthalpy:

h2 =h1+h2s -h1ηis       (6)

where ηis = 0.80 is the compressor isentropic efficiency. State 2 properties are determined from P₂ and h₂.

2.2.4 State 3 - Condenser Outlet (Subcooled Liquid)

State 3 is subcooled liquid that exists in the condenser:

P₃ = Pcond      (7)

T3= Tcond - ΔTsubcool     (8)

where ΔTsubcool = 3°C ensures liquid state before expansion.

2.2.5 State 4 - Expansion Valve Outlet (Two-Phase)

The expansion process is modeled as isenthalpic throttling:

h₄ = h₃     (9)

P₄ = Pevap     (10)

State 4 is typically in the two-phase region with quality x₄ between 0 and 1.

2.3 Energy Balance Analysis

The energy balance for the vapor compression cycle must satisfy the First Law of Thermodynamics. For the complete cycle operating at steady state

2.3.1 Evaporator Energy Balance

Heat absorbed in the evaporator (cooling capacity):

Qevap = ṁref × (h₁ - h₄)     (11)

This represents the useful cooling effect provided by the chiller.

2.3.2 Compressor Work

Work input to the compressor:

Ẇcomp = ṁref × (h₂ - h₁)     (12)

2.3.3 Condenser Heat Rejection

Heat rejected in the condenser:

Qcond = ṁref × (h₂ - h₃)     (13)

2.3.4 Overall Energy Balance Verification

Conservation of energy requires:

Qcond = Qevap + Ẇcomp     (14)

This relationship is verified in the model with an error tolerance of < 0.1%. The energy balance error is calculated as:

εenergy =Qcond - Qevap + ẆcompQcond × 100%     (15)

2.3.5 Coefficient of Performance

The COP quantifies cycle efficiency:

COP = QevapẆcomp     (16)

For the designed system with Tevap ≈ 2°C and Tcond ≈ 40°C, the model achieves COP ≈ 5.4.

2.4 Mass Conservation

Mass conservation in the refrigerant cycle requires constant mass flow rate through all components:

ṁref = Qevap / (h₁ - h₄)     (17)

The refrigerant mass flow rate is determined from the required cooling capacity and the specific enthalpy change across the evaporator. For the 1000 MW system, typical refrigerant mass flow rate is approximately 5000-6000 kg/s.

2.5 Water-Side Heat Exchanger Coupling

The refrigerant cycle is coupled to water circuits through the evaporator and condenser heat exchangers.

2.5.1 Evaporator (Chilled Water Side)

Energy balance on the chilled water:

Qevap = ṁCHW × cp,w × (TCHW,return - TCHW,supply)     (18)

where cp,w = 4186 J/(kg·K) is the specific heat of water. The chilled water mass flow rate is:

ṁCHW = Qevap / [cp,w × (TCHW,return - TCHW,supply)]     (19)

For 1000 MW cooling with ΔT = 5°C, ṁCHW ≈ 47,770 kg/s.

2.5.2 Condenser (Cooling Water Side)

Energy balance on the condenser water:

Qcond = ṁCW × cp,w × (TCW,out - TCW,in)     (20)

The condenser water flow rate is determined to achieve acceptable temperature rise while maintaining adequate heat transfer.

2.5.3 Pinch Point Constraints

Effective heat exchange requires minimum temperature differences (pinch points) between the refrigerant and water streams:

ΔTpinch,evap = TCHW,supply - Tevap ≥ 3°C     (21)

ΔTpinch,cond = Tcond - TCW,out ≥ 3°C     (22)

The iterative solver adjusts Tevap and Tcond to satisfy these constraints while converging to the required cooling capacity.

3. Cooling Tower Modeling

The cooling tower rejects condenser heat to the atmosphere through evaporative cooling. The model employs psychrometric analysis to accurately capture the heat and mass transfer processes.

3.1 Psychrometric Fundamentals

Moist air properties are calculated using the MoistAir class, which implements ASHRAE fundamental relationships:

3.1.1 Saturation Pressure

The saturation pressure of water vapor is calculated using the Antoine equation (ASHRAE formulation):

ln(Psat) = C₁/T + C₂ + C₃T + C₄T² + C₅T³ + C₆ln(T)     (23)

where T is in Kelvin and coefficients C₁-C₆ are empirical constants valid for -20°C to 50°C.

3.1.2 Humidity Ratio

The humidity ratio (specific humidity) relates to vapor and dry air masses:

w = 0.622 × Pv / (Patm - Pv)     (24)

where Pv = φ × Psat for a given relative humidity φ.

3.1.3 Specific Enthalpy

The specific enthalpy of moist air per unit mass of dry air:

h = cp ,da × T + w × (hfg,0 + cp,wv × T)     (25)

where cp,da = 1006 J/(kg·K), cp,wv = 1860 J/(kg·K), and hfg,0 = 2,501kJ/kg.

3.2 Cooling Tower Performance

3.2.1 Range and Approach

Two key parameters characterize cooling tower performance:

Range: The temperature drop of water through the tower:

Range = Twater,in - Twater,out     (26)

Approach: The difference between outlet water temperature and ambient wet bulb:

Approach = Twater,out - Twb     (27)

The design approach temperature is 4°C, representing practical heat transfer limitations.

3.2.2 Water Outlet Temperature

The water outlet temperature is determined by the approach:

Twater,out = Twb + Approach     (28)

For Twb = 24°C and Approach = 4°C; Twater,out = 28°C.

3.3 Energy Balance

The cooling tower energy balance couples heat rejection from water to heat absorption by air:

3.3.1 Water-Side Energy

Qwater = ṁCW × cp ,w × (Twater,in - Twater,out)     (29)

3.3.2 Air-Side Energy

The air absorbs both sensible and latent heat:

Qair = ṁda × (hair,out - hair,in)     (30)

where ṁda  is the dry air mass flow rate.

3.3.3 Energy Balance Solution

Conservation of energy requires Qwater = Qair. The model solves for air mass flow rate:

ṁda = Qwater / (hair,out - hair,in)     (31)

This approach ensures exact energy balance (< 0.1% error) rather than using a fixed air-to-water ratio.

3.4 Mass Balance and Water Consumption

3.4.1 Dry Air Conservation

Dry air mass is conserved through the tower:

ṁda,in = ṁda,out    (32)

3.4.2 Evaporation Rate

Water evaporates into the air stream, increasing humidity:

ṁevap = ṁda × (wout - win)     (33)

where wout and win  are the outlet and inlet humidity ratios.

3.4.3 Drift Loss

Small water droplets are carried out by air (drift eliminators reduce this):

ṁdrift = εdrift × ṁCW     (34)

where εdrift = 0.001% is the drift fraction.

3.4.4 Blowdown Rate

Blowdown prevents mineral concentration buildup:

ṁblowdown = ṁevap / (COC - 1)     (35)

where COC = 4 is the cycles of concentration.

3.4.5 Total Makeup Water

The total makeup water requirement:

ṁmakeup = ṁevap + ṁdrift + ṁblowdown     (36)

3.5 Fan Power Consumption

The cooling tower fan power is estimated as a fraction of heat rejection:

Ẇfan = 0.007 × Qcond     (37)

This empirical relationship (0.7% of heat rejected) accounts for typical induced-draft tower operation.

4. Pump System Modeling

The HVAC system includes condenser water pumps that circulate water between the chiller condenser and cooling tower.

4.1 Pump Power Calculation

Pump power is calculated from fluid mechanical principles:

Ẇpump =ρ × g × Htotal × Qηpump     (38)

where:

- ρ = 998 kg/m³ (water density)

- g = 9.81 m/s² (gravitational acceleration)

- Htotal = total head (m)

- Q̇ = ṁ/ρ = volumetric flow rate (m³/s)

- ηpump = 0.85 (pump efficiency)

4.2 Total Head Components

The total head consists of:

Htotal = Hstatic + Hdynamic + Hequipment     (39)

where Hstatic = 10 m (elevation change), and Hequipment = 6 m (heat exchanger and piping losses).

5. System Integration

5.1 Iterative Solution Procedure

The integrated CoolingSystem class employs an iterative solution to couple the chiller and cooling tower:

- Initialize condenser water inlet temperature estimate from cooling tower approach

- Solve chiller model for given cooling load, obtaining Qcond  and TCW,out

- Solve cooling tower model with condenser heat rejection, obtaining TCW,in new

- Check convergence: |TCW,innew - TCW,inold| < tolerance

- If not converged, update TCW,in and repeat from step 2

Convergence is typically achieved within 5-10 iterations with tolerance = 0.05°C.

5.2 Downstream Interface

The HVAC system provides the following outputs to downstream heat exchangers

| Parameter | Value | Description |
| --- | --- | --- |
| TCHW,supply | 7°C | CHW supply temperature |
| ṁCHW | 47,770 kg/s | CHW mass flow rate |
| Qcooling | 1000 MW | Total cooling capacity |
| COP | ~5.4 | System efficiency |

6. Modeling Assumptions

The following assumptions are made in the HVAC system model:

6.1 Refrigeration Cycle Assumptions

- Steady-state operation with constant mass flow rates

- Negligible pressure drops in evaporator and condenser piping

- Adiabatic expansion valve (isenthalpic process)

- Compressor isentropic efficiency ηis  = 0.80 (constant)

- Evaporator superheat = 5°C

- Condenser subcooling = 3°C

- R134a refrigerant properties from CoolProp (NIST Reference)

- Minimum pinch point temperature difference = 3°C

6.2 Cooling Tower Assumptions

- Induced-draft counterflow configuration

- Air exits at 95% relative humidity (near saturation)

- Approach temperature = 4°C (design condition)

- Atmospheric pressure = 101,325 Pa (standard)

- Lewis number ≈ 1 (equal heat and mass transfer)

- Drift loss = 0.001% of circulation rate

- Cycles of concentration (COC) = 4

- Fan power = 0.7% of heat rejection capacity

6.3 Water Properties Assumptions

- Constant specific heat cp,w = 4186 J/(kg·K)

- Constant density ρw = 998 kg/m³

- Incompressible flow

7. Performance Results

The integrated HVAC system achieves the following performance metrics under design conditions:

7.1 Energy Performance

| Component | Power (MW) | % of Total Load |
| --- | --- | --- |
| Chiller Compressor | 185.8 | 18.6% |
| Cooling Tower Fan | 8.3 | 0.8% |
| Condenser Water Pump | 9.3 | 0.9% |
| Total HVAC Power | 203.4 | 20.3% |

7.2 Water Consumption

| Parameter | Value | Unit |
| --- | --- | --- |
| Evaporation Rate | 681 | kg/s |
| Total Makeup Water | 909 | kg/s |
| Annual Water Consumption | 28.7 million | m³/year |
| WUE (Water Use Effectiveness) | 3.27 | L/kWh |

8. Conclusion

This report presented a comprehensive thermodynamic model for the HVAC cooling system of a 1 GW AI data center. The key findings include:

- The vapor compression chiller achieves COP ≈ 5.4 with R134a refrigerant, providing 1000 MW cooling capacity with approximately 186 MW compressor power input.

- Energy and mass balances are verified with errors < 0.1%, ensuring thermodynamic consistency.

- The cooling tower effectively rejects approximately 1186 MW of heat (Qevap  + Wcomp ) to the atmosphere through evaporative cooling.

- Total HVAC power consumption is approximately 203 MW, representing 20.3% overhead relative to the Total cooling load.

- The system interfaces seamlessly with downstream Building HX and Compute HX through a 7°C chilled water supply.

The model provides a rigorous thermodynamic foundation for system design and optimization, enabling accurate performance prediction under varying operating conditions.

References

ASHRAE. (2021). ASHRAE Handbook - Fundamentals. American Society of Heating, Refrigerating and Air-Conditioning Engineers.

Bell, I. H., Wronski, J., Quoilin, S., & Lemort, V. (2014). Pure and pseudo-pure fluid thermophysical property evaluation and the open-source thermophysical property library CoolProp. Industrial & Engineering Chemistry Research, 53(6), 2498-2508.

Cengel, Y. A., & Boles, M. A. (2015). Thermodynamics: An Engineering Approach (8th ed.). McGraw-Hill Education.

Kröger, D. G. (2004). Air-cooled Heat Exchangers and Cooling Towers. PennWell Books.

McQuiston, F. C., Parker, J. D., & Spitler, J. D. (2005). Heating, Ventilating, and Air Conditioning: Analysis and Design (6th ed.). John Wiley & Sons.